## Introduction
Low Carbon Concrete Mix Selection Tool - Introduction
Refer to the Low Carbon Concrete Mix Selection Tool Practical Implementation Guide for steps for use.
Ownership and accountability
Experience and/or knowledge of concrete mixes is required by personnel operating the Tool. This skillset may come from personnel with materials engineering and/or sustainability backgrounds. ​
The roles and responsibilities of the personnel required to operate/adapt the parameters in the Tool need to be determined beforehand by the individual water corporation. ​
Collaboration between Designers and Engineers, Sustainability, Procurement and Delivery at a minimum is necessary to use the Tool to achieve the best outcomes, as illustrated below.
Input tool owner and contributors to allow for review and oversight of process and outcomes in Table 1 and Table 2 below.
Table 1
Tool owner |  | Organisation/ position |  | Last review
Name |  | Position |  | DD/MM/YYYY
Table 2
Tool contributors |  | Organisation/ position |  | Last review
Name |  | Position |  | DD/MM/YYYY
Tool overview
The Tool is focused on concrete elements and is aligned to the Melbourne Retail Water Agencies (MRWA) database and Water Services Association of Australia (WSAA) standards. The Tool allows for the collation of information on appropriate concrete mixes in one place and prompts the user to consider higher supplementary cementitious materials (SCM)% mixes for water utility assets.
Input parameters
Project specifications: Input or review tool (Concrete Element Summary tab – refer to Figure 2) for project details such as type of structure (e.g., pipe, tank, pit), and exposure conditions (e.g., environmental factors).
Materials data: Review tool for, or gather data on, available concrete mixes including supplementary cementitious materials (e.g., fly ash, slag), aggregates, and admixtures from suppliers. Input mix information from suppliers in the Mix Details tab – refer to Figure 3.
Sustainability requirements: Understand project sustainability requirements and how that may be achieved with concrete reduction.
Using the Tool
1.Using project specification, review Concrete Element Summary tab to understand if the concrete asset type / elements required for the project are included in it:
a) If included: Review entry and update or include a new line if changes to Design Life (column D), WSAA requirements (column G), Exposure Classification (column I) are required.
b) If not included: Add a new line and include requirements for concrete based on standards.
ASSET TYPE | ELEMENT | DESIGN LIFE (YRS) | CONCRETE GRADE (MPa) | MINIMUM CEMENT CONTENT AS PER PROJECT SPECFIICATIONS, VR610 or WSAA (kg/m3) where relevant | WSAA, PROJECT OR ORGANISATION REQUIREMENTS / STANDARDS | UPPER LIMIT OF CEMENT (kg/m3) | EXPOSURE CONDITIONS (AS5100.5, AS3600, AS3735 or equivalent) | CONCRETE COVER (MM)
[8 empty] | MINIMUM DURABILITY COVER (mm) | ADDITIONAL CONSTRUCTION COVER IF CAST AGAINST GROUND OR BLINDING/DPM (mm)
B | C | D | E | F | G | H | I | J | K
Asset type breakdown |  | Required design life of element | Strength grade | Concrete requirements to VicRoads, WSAA, organisation or equivalent |  | Max cement if required | Explore classification to Australian Standards or equivalent | Required cover to reinforcement
2. Review concrete information in Concrete Element Summary tab for elements and determine if the following are applicable:
a) Do the mixes meet the requirements of the project (workability, sustainability, concrete type)?
b) Are the mixes available?
c) Will there be significant cost implications to the project?
3. Once the requirements of steps 1 & 2 are satisfied, move forward with design, procurement and construction following organisational processes.
SCM% | Coarse Aggregate (Y/N) |  |  | Fine Aggregate (Y/N) |  |  |  | Water (Y/N)
| Virgin Aggregate | Crushed Concrete | Plastic Aggregate | Virgin Aggregate | Manufactured Sand | Glass Fines | Recycled washed Sand | Potable Water | Recycled Water
If setting a min. or approx. SCM value | Aggregates proposed and their % or amount | [6 empty] | Water to be used
Potential Suppliers and their products |  |  |  |  | Is it recyclable at the End-of-life? | Trial Opportunity? [Y/N] | Potential Concrete Mixes and Details | Curing and Workability (Required changes to construction process) | Recommended text for Drawing Notes | Carbon Footprint
B: Hanson; C: Boral; D: Holcim; E: Other; F: Other | Carbon footprint outcome | EPDs
V | W | X | Y | Z | AA | AB | AC | AD | AE | (comment or value) | (link)
Potential mixes from suppliers that meet requirements. |  |  |  |  | Is there an opportunity to recycle the elements at end of life? | Is there an opportunity to do a mix trial on a new mix? | Mix and durability details, what's been used and what the options are. | Commentary on construction considerations. | Notes to add to drawings to ensure correct mixes placed. | Comment or value of expected or final outcome carbon footprint. | Hyperlink to copy of EPD if acquired.
4. If the Tool does not include the relevant mix information relevant for the project:
a) Contact concrete suppliers for additional mix information for project.
b) Add new mixes to Mix Details tab to assess cement and/or carbon reduction and compare properties.
i. Include information from concrete suppliers on mix specifications (Project Details columns B-E; Concrete Mix Details columns F-M; Cementitious Material columns N-Y; Aggregates columns Z-AG; Water to Cement ratio columns AH-AI); Performance Test Results columns AS-BA).
ii. The Tool will calculate the Cement Reduction % from a GBCA baseline (columns BB-BD) once step i. is complete.
iii. The Tool can be used to compare mixes on performance properties such as drying shrinkage, slump, VPV and admixtures used (columns AS-BA and AJ-AR). It can also compare carbon footprint information collected (columns BE-BF).
iv. Record any approval and compliance records for mixes to specifications or authorities (columns BG-BK).
5. Add any information collected and used into the Concrete Element Summary tab including:
a) Mix details including aggregates, SCM% and admixtures.
b) Availability, workability and process notes (from project team and contractors).
c) Drawing notes used.
d) Investigated trial mixes if relevant.
Most details should be included on a mix design document received from concrete suppliers.
Cement Reduction from GBCA baseline
% SCM content | GBCA Cement % Saving from Base Case | GBCA Cement % Saving from Base Case if incl 7.5% lime in OPC
Cells calculate cement savings from GBCA baseline.

## Concrete Element Summary
Concrete Mixes per Element
Add elements to the list and fill in requirements. Use to list what mixes may be useful for different applications with focus on replacing Portland Cement (OPC) with Supplementary Cementitious Materials (SCM)s
ASSET TYPE | ELEMENT | DESIGN LIFE (YRS) | CONCRETE GRADE (MPa) | MINIMUM CEMENT CONTENT AS PER PROJECT SPECIFICATIONS, DTP Section 610 or WSAA (kg/m3) where relevant | WSAA, PROJECT OR ORGANISATION REQUIREMENTS / STANDARDS | UPPER LIMIT OF CEMENT (kg/m3) | EXPOSURE CONDITIONS (AS5100.5, AS3600, AS3735 or equivalent) | CONCRETE COVER (MM) 1. Where curing compounds used, in B1 environments increase cover by 5 mm and in B2 or C1 environments by 10mm. 2. Increase cover by 30mm where cast against ground and by 10 mm where cast against blinding or a damp proof membrane. |  | SCM% | Coarse Aggregate |  | Fine Aggregate |  |  | Water | Potential Suppliers and their products |  |  |  |  | Is it recyclable at the End-of-life? | Trial Opportunity? [Y/N] | Potential Concrete Mixes and Details | Curing and Workability (Required changes to construction process) | Recommended text for Drawing Notes | Carbon Footprint
[8 empty] | MINIMUM DURABILITY COVER (mm) | ADDITIONAL CONSTRUCTION COVER IF CAST AGAINST GROUND OR BLINDING/DPM (mm) |  | Crushed Concrete | Plastic Aggregate (or other recycled waste aggregate) | Manufactured Sand | Glass Fines | Recycled washed Sand | Recycled Water | Hanson | Boral | Holcim | Other | Other | [5 empty] | Carbon footprint outcome | EPDs
B | C | D | E | F | G | H | I | J | K | L | N | O | Q | R | S | U | V | W | X | Y | Z | AA | AB | AC | AD | AE | (comment or value) | (link)
Temporary construction | Any non-permanent concrete (e.g. blinding, temporary protection, mass fill, crane pads, lay down areas, etc | Just for construction | As required, min 20 MPa | Push as low as possible - temp structures do not need to conform to DTP 610 - and base mixes on strength achieved via trials. | WSA PS-357 | TBC | N/A | N/A | N/A | up to 70% | 20% or | 10% plastic or 10% crumb rubber | or 50% | or 50% | Up to 25% | Now BAU | Gold Mix 50% SCM 20% CC 70% Recycled water | Envirocrete | Ecopact (>30% reduction in carbon emissions) | lower strength mixes | Geopolymer mix with emesh or 70% minimum SCM content. Calcined clay | Suggest testing to prove it meets project / utility requirements | Yes, as various water utilities undertake trials preference would be to share outcomes for all utilities benefit rather than each utility undertaking all trials | Cementitious binder to be at least 70% SCM; for coarse aggregates use either 20% recycled concrete aggregate, or 10% recycled plastic aggregate, or 10% crumbed rubber; fine aggregate - 50% manufactured sand and 50% recycled glass fines (unwashed). Note the potential use of recycled soil removed during site excavations is also being investigated. | General info: Boral's ENVISIA - Similar early age strength to GP/FA mixes, lower shrinkage (400 microstrain) Hanson - ECOTERA - Similar Early age strength to standard post-tensioned concrete. Lower shrinkage (250um to 450um) Holcim ECOPact - Placed, pumped and finished like conventional concrete. | Example: - PROVIDE A MINIMUM TOTAL OF 50% SUPPLEMENTARY CEMENTITIOUS MATERIAL ACROSS ALL IN SITU CONCRETE IN ACCORDANCE WITH THE VICROADS 610 STANDARD. - PROVIDE A MINIMUM TOTAL OF 65% SUPPLEMENTARY CEMENTITIOUS MATERIAL BY MASS ACROSS PILING IN ACCORDANCE WITH VICROADS 610 STANDARD. - PROVIDE A MINIMUM TOTAL OF 30% SUPPLEMENTARY CEMENTITIOUS MATERIAL BY MASS ACROSS ALL PRECAST CONCRETE ELEMENTS IN ACCORDANCE WITH XXXXX STANDARD. - INCORPORATE 25% RECYCLED MANUFACTURED SAND AS A REPLACEMENT OF TOTAL MASS OF FINE AGGREGATE IN CONCRETE MIX. - INCORPORATE 25% RECYCLED COARSE AGGREGATE OF TOTAL MASS OF COARSE AGGREGATE IN CONCRETE MIX. | tbc | Boral: https://epd-australasia.com/wp-content/uploads/2022/03/SP02341-Boral-EPD_2022_Vic_v1.0.pdf Holcim: https://epd-australasia.com/wp-content/uploads/2022/01/SP04657-Holcim-EPD-Victoria-ECOPact-Range_v5_Apr24.pdf
SUPs | SHARED USER PATH (SUP) | Design life on a case to case basis | Generally 32MPa, can be lower depending on use | VicRoads 32MPa 330kg/m3 (but should challenged) | N/A | 330kg/m3 | A or B1 (check local conditions) | 40 | +10 (total min 50) | up to 70% | 20% or | 10% plastic or 10% crumb rubber | or 50% | or 50% | Up to 25% | Now BAU | tbc | tbc | 49% SCM; 54% reduction from Greenstar 19.B.1 baseline; 100% recycled water used | lower strength mixes | Geopolymer mix with Emesh or 70% minimum SCM content. Calcined clay | Likely | N/A | Would expect 32 MPa mixes would be mainly used/required. Working with all concrete suppliers should be able to readily achieve a mix with a cementitious binder with at least 70% SCM content. Geopolymer once available. Potential to look at calcined clay. | Generally use of moisture curing and sealed curing rather than use of curing compound get better results All mixes can be provided in a range of slumps so discuss with the concrete supplier and construction team what works best for everyone | Consideration of guidance above as applicable to project and structure | tbc | tbc
Thrust Restraints | Thrust Restraint Blocks | Generally the same as the design life of the pipeline | As required, min 20 MPa | N/A | WSA PS-357 minimum cement required for required strength Normal Type Concrete | TBC | A or B1 (check local conditions) | TBC - per environmental conditions | TBC - per environmental conditions | up to 80% or geopolymer | 20% or | 10% plastic or 10% crumb rubber | 30% | or 30% | Up to 25% | Now BAU | tbc | tbc | tbc | lower strength mixes | N/A | Likely | N/A | Working with all concrete suppliers should be able to readily achieve a mix with a cementitious binder with at least 70% SCM content. Geopolymer once available. Potential to look at calcined clay. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Structure | Precast Panels | 100 | 50 | 450 kg/m3 (but should be challenged) | NA | 450 kg/m3 | B1 & B2 (check local soil conditions) | 40 | N/A | up to 50% | investigate use | investigate use | Up to 25% | investigate use | investigate use | Now BAU | Hanson/RECO Ecotera 50% SCM mix | Boral, 50MPa, 90 mins, 20mm ag, 120 slump | tbc | N/A | N/A | Likely | N/A | Hanson/RECO ecotera 50% SCM mixes available in 180mm and 650mm slumps. | tbc | Consideration of guidance above as applicable to project and structure | tbc | Handon: https://epd-australasia.com/wp-content/uploads/2023/11/SP10204-Hanson-EPD-Ecotera-VIC_Oct23.pdf
Drainage system | Pipes | 100 | 40 | DTP 40MPa 400kg/m3 (but should be challenged), AS/NZS 4058 ≥ 330kg/m3, w/c ≤0.4 | N/A | 400 kg/m3 | B1 & B2 (check local soil conditions) | 50 (VR standard drawings) | N/A | up to 80% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | tbc | tbc | tbc | N/A | Reinforced Concrete Pipes Australia - 80% SCM content ROCLA - | Likely | N/A | Investigate recycled plastics for pipes where possible. | tbc | Consideration of guidance above as applicable to project and structure | tbc | N/A
Sewerage System | Sewerage Storage Tank - Walls | 100 | 40 | 350kg/m3 (WSA 114) | Special Type Concrete | 400 kg/m3 | TBC per site conditions | TBC - per environmental conditions | TBC - per environmental conditions | up to 80% or geopolymer | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | Hanson, 50MPa, 90mins, 220 Slump | Boral, 40MPa, 650 slump, 14mm ag, SCC | Holcim, 40MPa, 10mm ag, 650 slump | N/A | N/A | Suggest testing to prove it meets project / utility requirements | Yes, as various water utilities undertake trials preference would be to share outcomes for all utilities benefit rather than each utility undertaking all trials | Investigate other materials. High slag content recommended for sewerage. Min 65%. Geopolymer once its available. Minimise shrinkage for tanks to reduce cracking. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Sewerage System | Sewerage Storage Tank - Slab | 100 | 40 | 350kg/m3 (WSA 114) | Special Type Concrete | 400 kg/m3 | TBC per site conditions | TBC - per environmental conditions | TBC - per environmental conditions | up to 80% or geopolymer | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | tbc | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) | Holcim, 55MPa, 20mm ag, 150 slump | N/A | N/A | Suggest testing to prove it meets project / utility requirments | Yes, as various water utilities undertake trials preference would be to share outcomes for all utilities beneift rather than each utility undertaking all trials | Investigate other materials. High slag content recommended for sewerage. Min 65%. Geopolymer once its available. Minimise shrinkage for tanks to reduce cracking. | tbc | Consideration of guidence above as applicable to project and structure | tbc | tbc
Sewerage System | Sewerage Storage - Pipes | 100 | As Per AS/NZS 4058 | N/A | WSA PS-233 WSA 113 | N/A | N/A | N/A | N/A | >25% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | tbc | tbc | tbc | N/A | Reinforced Concrete Pipes Australia - 80% SCM content ROCLA - | Suggest testing to prove it meets project / utility requirements | Yes, as various water utilities undertake trials preference would be to share outcomes for all utilities benefit rather than each utility undertaking all trials | Concrete pipe to satisfy the requirements of AS 4058 for appropriate class environments. ≥ 25% SCM. Investigate recycled plastics for pipes where possible. | tbc | Consideration of guidance above as applicable to project and structure | tbc | N/A
Chambers and Maintenance holes | Maintenance Holes for Non-Pressure Applications – Gravity Sewerage | 100 | 50 (SR) (WSA PS-323, WSA PS-331) | 450kg/m3 (WSA PS-323, WSA PS-331) | WSA PS-323, WSA PS-331 Min cement content = 450 kg/m3 (could be challenged to be total for binder content) | 450 kg/m3 | TBC per site conditions | Precast: 40 internally, 25 externally, 20 at joints | N/A | up to 80% or geopolymer | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | Hanson, 50MPa, 90mins, 200 Slump | Boral, 50MPa, 90 mins, 20mm ag, 120 slump | tbc | N/A | N/A | Suggest testing to prove it meets project / utility requirements | Yes, as various water utilities undertake trials preference would be to share outcomes for all utilities benefit rather than each utility undertaking all trials | Type SR for larger diameter holes, or even geopolymer concrete - see trial recommendation in item below. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Chambers and Maintenance holes | Conical Bases for Concrete Maintenance Holes (MH) for Non-Pressure Applications – Gravity Sewerage | 100 | 50 (SR) (WSA PS-333, Type SR) | 450kg/m3 (WSA PS-333) | WSA PS-333 Min cement content = 450 kg/m3 (could be challenged to be total for binder content) | 450 kg/m3 | TBC per site conditions | Precast: 40 internally, 25 externally, 20 at joints | N/A | up to 80% or geopolymer | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | Hanson, 50MPa, 90mins, 200 Slump | Boral, 50MPa, 90 mins, 20mm ag, 120 slump | tbc | N/A | N/A | Suggest testing to prove it meets project / utility requirements | Yes, as various water utilities undertake trials preference would be to share outcomes for all utilities benefit rather than each utility undertaking all trials | Where these elements are precast they would lend themselves to being fabricated from geopolymer concrete (0% GP cement). Highly worth a trial. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Drainage system | Detention tank - Walls | 100 | 50 | AS 3735 Min cement content = 320 kg/m3 (could be challenged to be total for binder content) | AS 3735 Min cement content = 320 kg/m3 (could be challenged to be total for binder content) | 450 kg/m3 | B1 & B2 (check local soil conditions) | 30mm cast against standard formwork | N/A | 60% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | Hanson, 50MPa, 90mins, 200 Slump | tbc | tbc | N/A | N/A | Likely | N/A | Minimise shrinkage for tanks to reduce cracking. Have specified 50MPa DTP approved concrete, 60% GGBFS, Cement aid Everdure CALTITE Hydrophobic Pore-Blocking ingredient (HPI) dosed at a rate of 30L/cubic meter of concrete or approved and tested alternative on recent project. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Drainage system | Detention tank - Slab | 100 | 40 | AS 3735 Min cement content = 320 kg/m3 (could be challenged to be total for binder content) | AS 3735 Min cement content = 320 kg/m3 (could be challenged to be total for binder content) | 400 kg/m3 | B1 & B2 (check local soil conditions) | 45mm cast against standard formwork | 55mm cast against blinding | up to 70% | 10% or | 10 kg/m3 | investigate use | investigate use | investigate use | Now BAU | tbc | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) | Holcim, 50MPa, 90mins, 120 slump | N/A | N/A | Likely | N/A | Minimise shrinkage for tanks to reduce cracking. Transport projects have specified 40MPa DTP approved concrete, - 50-70% GGBFS or - 30-40% FA or - 20-30% FA, 30-50% GGBFS and 0-10% SF with Cement aid Everdure CALTITE Hydrophobic Pore-Blocking ingredient (HPI) dosed at a rate of 30L/cubic meter of concrete or approved and tested alternative on a recent project. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Drainage system | Detention tank - Access Pit | 100 | 40 | AS 3735 Min cement content = 320 kg/m3 (could be challenged to be total for binder content) | N/A | 400kg/m3 | B1 & B2 (check local soil conditions) | 30mm cast against standard formwork | 40mm cast against blinding. | up to 70% | 10% or | 10 kg/m3 | investigate use | investigate use | investigate use | Now BAU | Hanson, 40MPa, 180 slump, | tbc | tbc | N/A | N/A | Likely | N/A | Transport projects have specified 40MPa DTP approved concrete, - 50-70% GGBFS or - 30-40% FA or - 20-30% FA, 30-50% GGBFS and 0-10% SF. On a recent project | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Drainage system | Detention tank - Outlet Pit | 100 | 40 | AS 3735 Min cement content = 320 kg/m3 (could be challenged to be total for binder content) | N/A | 400 kg/m3 | B1 & B2 (check local soil conditions) | 30mm cast against standard formwork | 40mm cast against blinding. | up to 70% | 10% or | 10 kg/m3 | investigate use | investigate use | investigate use | Now BAU | Hanson, 40MPa, 180 slump, | tbc | tbc | N/A | N/A | Likely | N/A | Transport projects have specified 40MPa DTP approved concrete, - 50-70% GGBFS or - 30-40% FA or - 20-30% FA, 30-50% GGBFS and 0-10% SF. On a recent project | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Drainage system | Detention tank - Outlet Pipe | 100 | As Per AS/NZS 4058 | N/A | N/A | N/A | N/A | N/A | N/A | >25% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | tbc | tbc | tbc | N/A | Reinforced Concrete Pipes Australia - 80% SCM content ROCLA - | Likely | N/A | Concrete pipe to satisfy the requirements of AS 4058 for appropriate class environments. ≥ 25% SCM. Investigate recycled plastics for pipes where possible. | tbc | Consideration of guidance above as applicable to project and structure | tbc | N/A
Drainage system | Roadway drainage pit - DTP Pits | 100 | 32 | VicRoads 32MPa 330kg/m3 (but should challenged) | N/A | 330 kg/m3 | B1 & B2 (check local conditions) | 50mm cast against standard formwork | 60mm cast against blinding. | up to 70% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | tbc | tbc | tbc | N/A | N/A | Likely | N/A | DTP approved mix, - 50-70% GGBFS or - 30-40% FA or - 20-30% FA, 30-50% GGBFS and 0-10% SF. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Structure | Structural Walls - Buried | 100 | 40 | VicRoads 40MPa 400kg/m3 (but should be challenged) | N/A | 400 kg/m3 | B1 & B2 (check local conditions) | TBC - per environmental conditions | TBC - per environmental conditions | up to 70% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU |  | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) Boral, 50MPa, 100 slump, 20mm ag | Holcim, 40MPa, 90mins, 120 slump | N/A | N/A | Likely | N/A | tbc | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Structure | Structural Walls - Non- Buried | 100 | 40 | VicRoads 40MPa 400kg/m3 (but should be challenged) | N/A | 400 kg/m3 | A or B1 (check local conditions) | TBC - per environmental conditions | TBC - per environmental conditions | up to 70% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU |  | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) Boral, 50MPa, 100 slump, 20mm ag | Holcim, 40MPa, 90mins, 120 slump | N/A | N/A | Likely | N/A | tbc | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Water Retaining - Potable | Potable Water - Tank Walls | 100 | 40 | 320kg/m3 as per AS 3735 | No information identified | No information identified | TBC per site conditions | TBC - per environmental conditions | TBC - per environmental conditions | up to 70% | investigate use | investigate use | investigate use | investigate use | investigate use | Check compliance with AS 4020 | Hanson, 50MPa, 90mins, 220 Slump | Boral, 40MPa, 650 slump, 14mm ag, SCC | Holcim, 40MPa, 10mm ag, 650 slump | N/A | N/A | Likely | N/A | Investigate other materials. Minimise shrinkage for tanks to reduce cracking. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Water Retaining - Wastewater | Wastewater - Tank Walls | 100 | 40 | 320kg/m3 as per AS 3735 | No information identified | No information identified | TBC per site conditions | TBC - per environmental conditions | TBC - per environmental conditions | up to 70% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | Hanson, 50MPa, 90mins, 220 Slump | Boral, 40MPa, 650 slump, 14mm ag, SCC | Holcim, 40MPa, 10mm ag, 650 slump | N/A | N/A | Likely | N/A | Investigate other materials. Minimise shrinkage for tanks to reduce cracking. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Structure | Foundations/Piles | 100 | 40 | See AS 2159:2009/Amdt 1:2010 (PS-356) | See AS 2159:2009/Amdt 1:2010 (PS-356) | No information identified | B1 & B2 (check local soil conditions) | TBC - per environmental conditions | TBC - per environemental conditions | min 65% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | Hanson, 50MPa, 90mins, 220 Slump | Boral, 40MPa, 650 slump, 14mm ag, SCC | Holcim, 40MPa, 10mm ag, 650 slump | N/A | N/A | Will be challenging to extract. | N/A | tbc | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Water Retaining - Potable | Potable Water - Tank Slab | 100 | 40 | 320kg/m3 as per AS 3735 | No information identified | No information identified | TBC per site conditions | TBC - per environmental conditions | TBC - per environmental conditions | up to 70% | investigate use | investigate use | investigate use | investigate use | investigate use | Check compliance with AS 4020 | tbc | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) Boral, 50MPa, 100 slump, 20mm ag | Holcim, 40MPa, 90mins, 120 slump | N/A | N/A | Likely | N/A | Investigate other materials. Minimise shrinkage for tanks to reduce cracking. | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Water Retaining - Wastewater | Wastewater - Tank Slab | 100 | 40 | 320kg/m3 as per AS 3735 | No information identified | No information identified | TBC per site conditions | TBC - per environmental conditions | TBC - per environmental conditions | up to 70% | investigate use | investigate use | investigate use | investigate use | investigate use | Now BAU | tbc | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) Boral, 50MPa, 100 slump, 20mm ag | Holcim, 40MPa, 90mins, 120 slump | N/A | N/A | Likely | N/A | Investigate other materials. Minimise shrinkage for tanks to reduce cracking. | tbc | Consideration of guidence above as applicable to project and structure | tbc | tbc
Slabs | Chemical bunds | 100 | 32 | VicRoads 32MPa 330kg/m3 (but should challenged) | No information identified | No information identified | B1 & B2 (check local conditions) | TBC - per environemental conditions | TBC - per environemental conditions | up to 80% or geopolymer | investigate use | 10 kg/m3 | investigate use | investigate use | investigate use | Now BAU | tbc | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) Boral, 50MPa, 100 slump, 20mm ag | Holcim, 40MPa, 90mins, 120 slump | N/A | N/A | Wll depend on condition, contamination | Yes, as various water utilities undertake trials preference would be to share outcomes for all utilities beneift rather than each utility undertaking all trials | tbc | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc
Slabs | Equipment Slabs | 100 | 32 | VicRoads 32MPa 330kg/m3 (but should challenge) | No information identified | No information identified | B1 & B2 (check local conditions) | TBC - per environmental conditions | TBC - per environmental conditions | up to 70% | investigate use | 10 kg/m3 | investigate use | investigate use | investigate use | Now BAU | tbc | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) Boral, 50MPa, 100 slump, 20mm ag | Holcim, 40MPa, 90mins, 120 slump | N/A | N/A | Likely | N/A | tbc | tbc | Consideration of guidance above as applicable to project and structure | tbc | tbc

## Mix Details
Currently available mixes
Add mixes from suppliers to list to compare. Enter mix design details in green and yellow headed cells.
| Project Details - where mix has been used if applicable |  |  |  | Concrete Mix Details | [8 empty] | Cementitious Material | [11 empty] | Aggregates | [7 empty] | Water to Cement ratio |  | Admixtures | [8 empty] | Performance Test Results | [8 empty] | Cement Reduction from GBCA baseline |  |  | Carbon Footprint |  | Approval and Compliance
| Project Mix Code/ Date of Use | Project Reference | Elements | Link to copy of mix design | Mix Name (used in Concrete Element Summary) | Concrete Mix Supplier | ARRB/VicRoads/DTP Chart Number: | Mix Design No: | Company Mix No: | Concrete Type Description | Strength Grade (MPa @28d) | Strength @ 1d, 3d, 7d, 28d if available | Mix Type | Cement OPC (incl mineral addition) (kg/m3) | Cement Description | Cement Mineral Addition to OPC ~ 7.5% Lime | Cement OPC less mineral additions | SCM Flyash (FA) | SCM - FA details | SCM - Ground Granulated Blast Furnace Slag (GGBFS) | SCM - GGBFS details | SCM - Silica Fume (SF) | SCMl - SF details | Total Cementitious Content (kg/m3) | GBCA Reference Cementitious Content | Aggregate 1: | Aggregate 1: Description | Aggregate 2: | Aggregate 2: Description | Aggregate 3: | Aggregate 3: Description | Aggregate 4: | Aggregate 4: Description | Water (L) | W/C | Admixture 1: Aerator AE | Admixture 2: WR | Admixture 3:Retarder RE | Admixture 4: Accel AC | Admixture 5: HWR | Admixture 6: MWWR | Admixture 7: Viscosity Modifier | Admixture 8: Fibre | Admixture 9: Other | Slump (design) (mm): | Slump (tested) (mm): | Placement Time (mins T500) | J-Ring (jr mm) | VPV % | Drying Shrinkage microstrain @ 21d | Drying Shrinkage microstrain @ 56d | Soluble salts chloride % | Soluble salts sulphate % | % SCM content | GBCA Cement % Saving from Base Case | GBCA Cement % Saving from Base Case if incl 7.5% lime in OPC | Embodied Carbon (kgCO2eq) | EPD | WSAA or DTP Compliant | WSAA or DTP Approved | Fire Tested with Fibres | Fire Tested without Fibres | Project Recommended
filter | (Number/code) | (Name) | (element details) | (can hyperlink) | [11 empty] | (auto calc.) | (auto calc.) | [6 empty] | (auto calc.) | (auto calc.) | [9 empty] | (auto calc.) | [18 empty] | (auto calc.) | (auto calc.) | (auto calc.) | (value) | (link) | (Yes/No) | (Yes/No) | (Yes/No) | (Yes/No) | Comment
| example: Mix123 (12/04/2022) | example: Project B | example: Slab - Precast | Boral Multiple Plants (Western Region) - VR400.40 (6.90min') - VRA40AUU68 (60min') - VRA40AUU18 (90min') - G4502 - FA.pdf | Boral, 40 MPa, 60/90min, 80 slump, (Polyrok) | Boral | G4502-FA, ARRB Reference Number: PR-000995-C121 | 4502 | VRA40AUU68 | VR400/40 (60/90min’) (Polyrok) | 40MPa | n/a | 50% GGBF Slag | 200 | GP Cement - Boral Geelong - ATIC 236 | 15 | 185 | 0 | n/a | 200 | GGBF Slag - Steel Cement - ATIC 167 (50%) | 0 | n/a | 400 | 440 | 1100 | 14mm Graded Pebble - Boral Bacchus Marsh | 10 | Recycled Plastic – Polyrok | 630 | Natural Concrete Sand - Boral Bacchus Marsh | n/a | n/a | 180 | 0.45 | n/a | 400-1000 WRAc - Sikaplast Eco 3W (mL/100kg. cementitious) | 0-300 Re - Sika Retarder N (mL/100kg. cementitious) | n/a | n/a | n/a | n/a | n/a | n/a | 80(+-)15 | n/a | 60 | n/a | 13.6 | 500 | n/a | 0.07 | 4.07 | 50% | 54.55% | 57.95% |  |  |  | DTP Approved
| To be filled during use |  |  | Boral Multiple Plants (Western Region) - VR400.40 (6.90min') - VRA40AUU68 (60min') - VRA40AUU18 (90min') - G4502 - FA.pdf | Boral, 40MPa, 60/90min, 80 slump, (Polyrok) | Boral | G4502-FA, ARRB Reference Number: PR-000995-C121 | 4502 | VRA40AUU18 | VR400/40 (60/90min’) (Polyrok) | 40MPa | n/a | 50% GGBF Slag | 200 | GP Cement - Boral Geelong - ATIC 236 | 15 | 185 | 0 | n/a | 200 | GGBF Slag - Steel Cement - ATIC 167 (50%) | 0 | n/a | 400 | 440 | 1100 | 14mm Graded Pebble - Boral Bacchus Marsh | 10 | Recycled Plastic – Polyrok | 630 | Natural Concrete Sand - Boral Bacchus Marsh | n/a | n/a | 180 | 0.45 | n/a | 400-1000 WRAc - Sikaplast Eco 3W (mL/100kg. cementitious) | 0-300 Re - Sika Retarder N (mL/100kg. cementitious) | n/a | n/a | n/a | n/a | n/a | n/a | 80(+-)15 | n/a | 90 | n/a | 13.6 | 500 | n/a | 0.07 | 4.07 | 50% | 54.55% | 57.95% |  |  |  | DTP Approved
|  |  | PRECAST | RECO_DTP 50% Slag Ecotera_01.pdf, ZDT3418S5 - Results (Interim) - CTM9991.pdf | Hanson, 50MPa, 180 slump | Hanson | In Progress | N/A | ZDT3418S5 | VR450/50 | 50MPa | 12 (1d), 33.5 (3d), 55 (7d), 79.5 & 84 (28d) | DTP | 225 | Cement Australia Port Kembla GP Cement | 16.875 | 208.125 | 0 | n/a | 225 | Cement Australia Port Kembla GGBF Slag | 0 | n/a | 450 | 550 | 1030 | Boral Culcairn 14mm Aggregate | 750 | Wodonga Quarries Coarse Sand | 0 | Judd's Fine Sand | n/a | n/a | 180 | 0.4 | n/a | n/a | 0-300 Sika RE Retarder-N (mL/100kg) | n/a | 300-800 Sika HWR Plastiment 190-SC (mL/100kg) | n/a | n/a | n/a | n/a | 180 | 220 | n/a | n/a | 10.3 | 310 | 750 | n/a | n/a | 50% | 59.09% | 62.16%
|  |  | PRECAST | RECO_DTP 50% Slag Ecotera_01.pdf, ZDT3418E5 - Results (Interim) - CTM9992.pdf | Hanson, 50MPa, 180 slump, Ecotera | Hanson | In Progress | N/A | ZDT3418E5 | VR450/50 | 50MPa | 16.5 (1d), 34 (3d), 46 (7d), 50.5 & 53 (28d) | DTP | 225 | Cement Australia Port Kembla GP Cement | 16.875 | 208.125 | 0 | n/a | 225 | Cement Australia Port Kembla GGBF Slag | 0 | n/a | 450 | 550 | 1030 | Boral Culcairn 14mm Aggregate | 750 | Wodonga Quarries Coarse Sand | 0 | Judd's Fine Sand | n/a | n/a | 180 | 0.4 | n/a | n/a | 0-300 Sika RE Retarder-N (mL/100kg) | n/a | 300-800 Sika HWR Plastiment 190-SC (mL/100kg) | n/a | n/a | n/a | Hanson Ecotera Activating Additive | 180 | 160 | n/a | n/a | 13.9 | 200 | 750 | n/a | n/a | 50% | 59.09% | 62.16%
|  |  | PRECAST | RECO_DTP 50% Slag Ecotera_01.pdf, ZDT3465S5 - Results (Interim) - CTM9993.pdf | Hanson, 50MPa, 650 slump, SCC | Hanson | In Progress | N/A | ZDT3465S5 | VR450/50 | 50MPa | 9.9 (1d), 29.5 (3d), 51.5 (7d), 73 & 71 (28d) | DTP (SCC) | 225 | Cement Australia Port Kembla GP Cement | 16.875 | 208.125 | 0 | n/a | 225 | Cement Australia Port Kembla GGBF Slag | 0 | n/a | 450 | 550 | 850 | Boral Culcairn 14mm Aggregate | 840 | Wodonga Quarries Coarse Sand | 100 | Judd's Fine Sand | n/a | n/a | 180 | 0.4 | n/a | n/a | 0-300 Sika RE Retarder-N (mL/100kg) | n/a | 300-800 Sika HWR Plastiment 190-SC (mL/100kg) | n/a | n/a | n/a | n/a | 650 | 660 | n/a | n/a | 10.6 | 340 | 750 | n/a | n/a | 50% | 59.09% | 62.16%
|  |  | PRECAST | RECO_DTP 50% Slag Ecotera_01.pdf, ZDT3465E5 - Results (Interim) - CTM9994.pdf | Hanson, 50MPa, 650 slump, Ecotera, SCC | Hanson | In Progress | N/A | ZDT3465E5 | VR450/50 | 50MPa | 14.5 (1d), 33.5 (3d), 48.5 (7d), 62.5 & 57 (28d) | DTP (SCC) | 225 | Cement Australia Port Kembla GP Cement | 16.875 | 208.125 | 0 | n/a | 225 | Cement Australia Port Kembla GGBF Slag | 0 | n/a | 450 | 550 | 850 | Boral Culcairn 14mm Aggregate | 840 | Wodonga Quarries Coarse Sand | 100 | Judd's Fine Sand | n/a | n/a | 180 | 0.4 | n/a | n/a | 0-300 Sika RE Retarder-N (mL/100kg) | n/a | 300-800 Sika HWR Plastiment 190-SC (mL/100kg) | n/a | n/a | n/a | Hanson Ecotera Activating Additive | 650 | 560 | n/a | n/a | 12.9 | 250 | 750 | n/a | n/a | 50% | 59.09% | 62.16%
|  |  |  | Holcim - Multiple Plants - VS552FVRT - VR470.55 (HES) (90min') - VR Chart G3871-FA(updated 5.2.21).pdf | Holcim, 55MPa, 150 slump | Holcim | G3871-FA | 3871 | VS552FVRT | S55 20MM VR470 150SL HSCM CONC | 55MPa | 45 & 44 (3d), 59 & 58.5 (6d), 69 & 78 (27d) |  | 221 | CA - Goliath CMRS-ATIC 002 | 16.575 | 204.425 | 122 | Gladstone CMRS - ATIC-029 | 147 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 490 | 550 | n/a | not specified | n/a | not specified | n/a | n/a | n/a | n/a | 175 | 0.35714 | n/a | n/a | 0-250 (mL/100kg) - BASF POZZ 122Ri | n/a | 320-720 (mL/100kg) - BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | 150(+-)30 | 160 | n/a | n/a | 9.8 | 260 | 360 | 0.015 | 1.5 | 54.9% | 59.82% | 62.83% |  |  |  | DTP Approved
|  |  |  | VR400-40 ZDT2218SC (Test Reports).pdf | Hanson, 40MPa, 180 slump, | Hanson | In Progress | N/A | ZDT2218SC | VR400/40 | 40MPa | 7.5 (1d), 25 (3d), 34 & 37.5 (7d), 42 (14d), 55 (21d), 53 & 58.5 (28d) | n/a | n/a | n/a | #VALUE! | #VALUE! | n/a | n/a | n/a | n/a | n/a | n/a | 0 | 440 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a |  | #DIV/0! | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | 180 | 170 | n/a | n/a | 15.1 | 370 | 530 | 0.029 | 3.2 | #DIV/0! | #VALUE! | #VALUE!
|  |  |  | VR450-50 ZDT3218SC (Test Reports).pdf | Hanson, 50MPa, 180 slump, | Hanson | In Progress | S10396 | ZDT3218SC | VR450/50 | 50MPa | 9 (1d), 28.5 (3d), 38.5 & 40.5 (7d), 49.5 (14d), 58 (21d), 57.5 & 58.5 (28d), 71 & 69.5 (56d), 70 (91d) | n/a | n/a | n/a | #VALUE! | #VALUE! | n/a | n/a | n/a | n/a | n/a | n/a | 0 | 550 | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a |  | #DIV/0! | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a | n/a |  |  | n/a | n/a | 15.6 | 380 | 530 | 0.021 | 3.2 | #DIV/0! | #VALUE! | #VALUE!
[5 empty] | Boral, 40MPa, 60 mins, 14mm ag, 80 slump | Boral | In Progress | 3760 | VRA40AU048 | VR400/40 (60min) | 40MPa | not supplied | VR400/40 | 200 | GP Cement - Boral, Waurm Ponds - ATIC 172 | 15 | 185 | 0 | n/a | 200 | GGBF Slag - Steel Cement - ATIC 167 (50%) | 0 | n/a | 400 | 440 | 1120 | 14mm Graded Pebble - Boral Bacchus Marsh | 652 | Natural Concrete Sand - Boral, Bacchus Marsh | n/a | n/a | n/a | n/a | 180 | 0.45 | n/a | 400-800 WRRe - Sikaplast Eco 60 (mL/100kg. cementitious) | 0-300 Re - Sika Retarder N (mL/100kg. cementitious) | n/a | n/a | n/a | n/a | n/a | n/a | 80 (+-) 15 | n/a | 60 | n/a | 13.8 | 460 | n/a | 0.059 | 2.32 | 50% | 54.55% | 57.95%
|  |  |  | Boral - West Melbourne - VR400.40 (60.90min)- VRA40AU048 - VRA40AUR18 - G3760-FA_amended_140820.pdf | Boral, 40MPa, 90 mins, 14mm ag, 80 slump | Boral | G3760-FA | 3760 | VRA40AUR18 | VR400/40 (90min) | 40MPa | not supplied | VR400/40 | 200 | GP Cement - Boral, Waurm Ponds - ATIC 172 | 15 | 185 | 0 | n/a | 200 | GGBF Slag - Steel Cement - ATIC 167 (50%) | 0 | n/a | 400 | 440 | 1120 | 14mm Graded Pebble - Boral Bacchus Marsh | 652 | Natural Concrete Sand - Boral, Bacchus Marsh | n/a | n/a | n/a | n/a | 180 | 0.45 | n/a | 400-800 WRRe - Sikaplast Eco 60 (mL/100kg. cementitious) | 0-300 Re - Sika Retarder N (mL/100kg. cementitious) | n/a | n/a | n/a | n/a | n/a | n/a | 80 (+-) 15 | n/a | 90 | n/a | 13.8 | 460 | n/a | 0.059 | 2.32 | 50% | 54.55% | 57.95% |  |  |  | DTP Approved
|  |  |  | Boral - West Melbourne - VR400.40 (90min') - VRA40A2R1C - Oracle 206600 - Chart G3878-FA.pdf | Boral, 40MPa, 90 mins, 14mm ag, 120 slump | Boral | G3878-FA | 3878 | VRA40A2R1C | VR400/40 (90min) | 40MPa | not supplied | VR400/40 | 300 | GP Cement - ATIC 172 | 22.5 | 277.5 | 100 | Fly Ash - ATIC 022 (25% replacement) | n/a | n/a | 0 | n/a | 400 | 440 | 1080 | 14mm Graded Pebble - Boral Bacchus Marsh | 673 | Natural Sand - Boral, Bacchus Marsh | n/a | n/a | n/a | n/a | 180 | 0.45 | n/a | 400-800 WRRe - Sikaplast Eco 60 (mL/100kg. cementitious) | 0-300 Re - Sika Retarder N (mL/100kg. cementitious) | n/a | 0.5-2 Sika ViscoCrete 10 (L/m3) | n/a | n/a | n/a | n/a | 120 (+-) 30 | n/a | 90 | n/a | 11.6 | 520 | n/a | 0.072 | 2.4 | 25% | 31.82% | 36.93% |  |  |  | DTP Approved
|  |  |  | Boral 47% SCM Port Botany Counterfort Mix 3 -200mm Slump (2008).pdf | Boral, 50MPa, 90 mins, 20mm ag, 120 slump | Boral | In Progress | n/a | n/a | VR450/50, 47% SCM | 50MPa | 7 days: 44, 20 days: 70.5, 56 days: 77.5, 90 days: 84. | VR450/50 | 258 | Cement (BTSLA-BCSC) | 19.35 | 238.65 | 121 | Flyash (BC-ASH) 25% | 106 | Enviroment (Slag) 22% | 0 | n/a | 485 | 550 | 737 | 20mm BM (Peats Ridge) | 333 | 10mm BM (Peats Ridge) | 444 | Nepean Course Sand (Emu Plain) | 217 | Kurnell Fine Sand (Rocla) | 170 | 0.35052 | 0.72 ml/100kg MasterLife SRA (Formally Rheomac 1009) | n/a | n/a | n/a | 0.98 kg/m3 - MasterGlenium SKY 8100 | n/a | n/a | n/a | 3 kg/m3 - Tetraguard | 220 | 220 | 90 | n/a | n/a | n/a | 460 | 0.005 | 0.69 | 46.8% | 53.09% | 56.61%
|  |  |  | Boral Melbourne VR400.40, VRA40AURPV - 235433, VR Chart No.G3313-CA.pdf | Boral, 40MPa, 650 slump, 14mm ag, SCC | Boral | G3313-CA | 2413 | VRA40AURPV | VR400/40 SCC (120MIN) | 40MPa | not supplied | VR400/40 | 230 | GP Cement - Boral, Waurm Ponds | 17.25 | 212.75 | 0 | n/a | 230 | ICL GGBFS - Slag | 0 | n/a | 460 | 440 | 825 | 14mm Graded Pebble - Boral Bacchus Marsh | 835 | Natural Sand - Boral, Bacchus Marsh | n/a | n/a | n/a | n/a | 195 | 0.42391 | n/a | n/a | 100-400 mL/100kg - Sika Retarder N | n/a | 1-4 L/m3 - Sika Viscocrete PCHRF 2 | 400-1000 ml/100kg - Sika Eco80SK | 0-4 L/m3 - Sika VMA | n/a | n/a | 650 (+-) 100 | n/a | T500 3.5 | 10 | n/a | n/a | n/a | n/a | n/a | 50% | 47.73% | 51.65% |  |  |  | DTP - Conditionally Approved
|  |  |  | Boral mixes Ver10 Submission pages 1 to 3.pdf | Boral, 40MPa, 110 slump, 20mm ag | Boral | N/A | 141772 | 141772 | B80 40 Mpa 20mm B2 | 40MPa | not supplied | VR400/40 | 205 | SL/SR Cement | 15.375 | 189.625 | 115 | Fly Ash | 140 | Environement GGBFS | 0 | n/a | 460 | 440 | not supplied | n/a | n/a | n/a | n/a | n/a | n/a | n/a | not supplied | 0.41 | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 110 (+-) 20 | n/a | n/a | n/a | n/a | n/a | 650 | n/a | n/a | 55.43% | 53.41% | 56.9% | 229
|  |  |  | Boral mixes Ver10 Submission pages 1 to 3.pdf | Boral, 50MPa, 100 slump, 20mm ag | Boral | N/A | 141778 | 141778 | B80 50 Mpa 20mm B2 | 50MPa | not supplied | VR450/50 | 215 | SL/SR Cement | 16.125 | 198.875 | 150 | Fly Ash | 125 | Environement GGBFS | 0 | n/a | 490 | 550 | not supplied | n/a | n/a | n/a | n/a | n/a | n/a | n/a | not supplied | 0.4 | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 100 (+-) 20 | n/a | n/a | n/a | n/a | n/a | 650 | n/a | n/a | 56.12% | 60.91% | 63.84% | 236
|  |  |  | Boral NSW RMS B80 50MPa B2 Exposure Pump mix.pdf | Boral, 50MPa, 100 slump, 20mm ag, Pump Mix | Boral | N/A | 50PU230537 | 50PU230537 | B80 50 Mpa 20mm B2 - Pump Mix | 50MPa | not supplied | VR450/50 | 215 | Boral Cement - Berrima | 16.125 | 198.875 | 150 | Eraring Power Station | 125 | Boral Cement - Maldon | 0 | n/a | 490 | 550 | 790 | 20/14mm Agg - Pepper Tree Quarry | 340 | 10/7mm Agg - Pepper Tree Quarry | 330 | Manufactured Sand - Pepper Tree Quarry | 220 | Fine Sand - Stockton Quarry | 196 | 0.4 | n/a | n/a | 200 (mL/100kg) - SIKA Retarder N | n/a | n/a | n/a | 860 (mL/m3) - SIKA Viscocrete PCHRF2 | n/a | 350 (mL/100kg) - SIKA Plastiment 10 | 100 | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 56.12% | 60.91% | 63.84%
|  |  |  | Boral Wollert VR400-40 - 90min - spray - VRA407QRP7 - Oracle 232463, VR ....pdf | Boral, 40MPa, 70 slump, 7mm ag, Spray | Boral | G3536-FA | 2636 | VRA407QRP7 | VR400 (90 MIN) (SPRAY) | 40MPa | not supplied | VR400/40 | 330 | Boral Waurn Ponds - ATIC 172 | 24.75 | 305.25 | 70 | Flyash Australia - Mt Piper - ATIC 022 (16% SCM) | 0 | n/a | 40 | Sika Fume - STIC 610 (9% SCM) | 440 | 440 | 720 | 7mm Aggregate - Boral Wollert | 964 | Concrete Sand - Boral Bacchus Marsh | n/a | n/a | n/a | n/a | 198 | 0.45 | n/a | 400-800 (mL/100kg) - SikaPlast Eco 60 | 50-300 (mL/100kg) - SIKA Retarder N | n/a | 10 (L/m3) - SIKA Viscocrete PCHRF2 | n/a | n/a | n/a | n/a | 70 (+-) 15 | n/a | 90 | n/a | 14.4 | 630 | n/a | 0.068 | 1.76 | 25% | 25% | 30.63% |  |  |  | DTP Approved
|  |  |  | Hanson 50% SCM mix.pdf | Hanson, 50MPa, 90mins, 180 Slump | Hanson | G4604-FA, PR-000995-C224-1 | 4604 | ZDT3418T5 | VR450/50 (90MIN) (HIGH SCM) 180 slump | 50MPa | N/A | VR450/50 | 225 | Cement Australia Goliath ATIC 002 | 16.875 | 208.125 | 113 | Cement Australia Melbourne ATIC 029 | 113 | Steel Cement Port Melbourne ATIC 167 | 0 | n/a | 451 | 550 | 1090 | 14mm Course Agg - Kilmore Quarry | 540 | Natural course sand - Yannathan Quarry | 160 | Man Sand - Kilmore Quarry | n/a | n/a | 180 | 0.39911 | n/a | 0-1500 (mL/100kg) - SikaPlast 3in1 | 0-300 (mL/100kg) - Sika Retarder N | n/a | 0-700 (mL/100kg) - Sika ViscoCrete 10 | n/a | n/a | n/a | n/a | 180 (+-) 40 | n/a | 90 | n/a | 12.9 | 600 | n/a | 0.016 | 2.7 | 50.11% | 59.09% | 62.16% |  |  |  | ARRB/DTP Approved
|  |  |  | Hanson 50% SCM mix.pdf | Hanson, 50MPa, 90mins, 200 Slump | Hanson | G4604-FA, PR-000995-C224-1 | 4604 | ZDT3420T5 | VR450/50 (90MIN) (HIGH SCM) 200 slump | 50MPa | N/A | VR450/50 | 225 | Cement Australia Goliath ATIC 002 | 16.875 | 208.125 | 113 | Cement Australia Melbourne ATIC 029 | 113 | Steel Cement Port Melbourne ATIC 167 | 0 | n/a | 451 | 550 | 1090 | 14mm Course Agg - Kilmore Quarry | 540 | Natural course sand - Yannathan Quarry | 160 | Man Sand - Kilmore Quarry | n/a | n/a | 180 | 0.39911 | n/a | 0-1500 (mL/100kg) - SikaPlast 3in1 | 0-300 (mL/100kg) - Sika Retarder N | n/a | 0-700 (mL/100kg) - Sika ViscoCrete 10 | n/a | n/a | n/a | n/a | 200 (+-) 40 | n/a | 90 | n/a | 12.9 | 600 | n/a | 0.016 | 2.7 | 50.11% | 59.09% | 62.16% |  |  |  | ARRB/DTP Approved
|  |  |  | Hanson 50% SCM mix.pdf | Hanson, 50MPa, 90mins, 220 Slump | Hanson | G4604-FA, PR-000995-C224-1 | 4604 | ZDT3422T5 | VR450/50 (90MIN) (HIGH SCM) 220 slump | 50MPa | N/A | VR450/50 | 225 | Cement Australia Goliath ATIC 002 | 16.875 | 208.125 | 113 | Cement Australia Melbourne ATIC 029 | 113 | Steel Cement Port Melbourne ATIC 167 | 0 | n/a | 451 | 550 | 1090 | 14mm Course Agg - Kilmore Quarry | 540 | Natural course sand - Yannathan Quarry | 160 | Man Sand - Kilmore Quarry | n/a | n/a | 180 | 0.39911 | n/a | 0-1500 (mL/100kg) - SikaPlast 3in1 | 0-300 (mL/100kg) - Sika Retarder N | n/a | 0-700 (mL/100kg) - Sika ViscoCrete 10 | n/a | n/a | n/a | n/a | 220 (+-) 40 | n/a | 90 | n/a | 12.9 | 600 | n/a | 0.016 | 2.7 | 50.11% | 59.09% | 62.16% |  |  |  | ARRB/DTP Approved
|  |  |  | Holcim - Multiple Plants - VS402FVRT - VR400.40 (HES) (90min') - VR Chart G3869-FA(updated 5.2.21).pdf | Holcim, 40MPa, 90mins, 120 slump | Holcim | G3869-FA | 3869 | VS402FVRT | VR400/40 (HES) (90mins) | 40MPa | n/a | VR400/40 (HES) (90mins) | 200 | CA - Goliath CMRS-ATIC 002 | 15 | 185 | 80 | Gladstone CMRS - ATIC-029 | 120 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 400 | 440 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 175 | 0.4375 | n/a | 260-460 (mL/100kg) - BASF MasterPolyheed 8190 | 0-250 (mL/100kg) - BASF POZZ 122Ri | n/a | 0-400 (mL/100kg) - BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | 120(+-)30 | n/a | 90 | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 50% | 54.55% | 57.95% |  |  |  | DTP Approved
|  |  |  | Holcim - Multiple Plants - VS502FVRT - VR450.50 (HES) (90min') - VR Chart G3870-FA(updated 5.2.21).pdf | Holcim, 50MPa, 90mins, 120 slump | Holcim | G3870-FA | 3870 | VS502FVRT | VR450/50 (HES) (90mins) | 50MPa | n/a | VR450/50 (HES) (90mins) | 230 | CA - Goliath CMRS-ATIC 002 | 17.25 | 212.75 | 92 | Gladstone CMRS - ATIC-029 | 138 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 460 | 550 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 175 | 0.38043 | n/a | 260-460 (mL/100kg) - BASF MasterPolyheed 8190 | 0-250 (mL/100kg) - BASF POZZ 122Ri | n/a | 0-400 (mL/100kg) - BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | 120(+-)30 | n/a | 90 | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 50% | 58.18% | 61.32% |  |  |  | DTP Approved
|  |  |  | Holcim 30% SCM VS502VR 2019-115 50MPA HES with Fibres.pdf | Holcim, 50MPa, 20mm ag 150 slump, Fibres | Holcim | In Progress | Not supplied | VS502FVF3 / VPROFM027 | S50 20mm VR450 150mmSL Fibre Conc | 50MPa | n/a | VR450/50 | 346 | CA - Goliath CMRS-ATIC 002 | 25.95 | 320.05 | 144 | Gladstone CMRS - ATIC-029 | 0 | n/a | 0 | n/a | 490 | 550 | 740 | 20/14mm Agg - Holcim - Pakenham | 318 | 10/7mm Agg - Holcim - Pakenham | 523 | Natural Sand - Holcim - Grantville | 175 | Man Sand - Holcim Tynong | 190 | 0.38776 | n/a | n/a | 0-100 (mL/100kg) - BASF POZZ 122Ri | n/a | 350-550 (mL/100kg) - BASF MasterGlenium SKY 8455 | n/a | n/a | Proflex Fibremesh 150 - 12 Fibre 2.7kg/m3 | n/a | 150(+-)30 | n/a | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 29.39% | 37.09% | 41.81%
|  |  |  | Holcim high SCM mixes & 40MPa with 70% .pdf | Holcim, 40MPa, 20mm ag, 120 slump | Holcim | In Progress | Not supplied | VE402EVR2 | S40 20MM VR400 120SL Ecopact Conc | 40MPa | n/a | VR400/40 | 200 | CA - Goliath CMRS-ATIC 002 | 15 | 185 | 80 | Melbourne CMRS - ATIC-029 | 120 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 400 | 440 | 670 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 175 | 0.4375 | n/a | BASF MasterPolyheed 8190 | BASF - MasterSet RT 122 | BASF - MasterSet AC 534 | BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | 120 | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 50% | 54.55% | 57.95%
|  |  |  | Holcim high SCM mixes & 40MPa with 70% .pdf, VE401VWCH.pdf | Holcim, 40MPa, 10mm ag, 650 slump | Holcim | G4503-FA | 4503 | VE401VWCH | S40 10mm 650SP 70% SCM Ecopact VR400 Conc | 40MPa | n/a | VR400/40 | 132 | CA - Goliath CMRS-ATIC 002 | 9.9 | 122.1 | 150 | Melbourne CMRS - ATIC-029 | 158 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 440 | 440 | 756 | 10mm Agg - Oaklnads Junction Blend | 698 | Washed concrete sand - Grantville Sand Plant | 236 | Man Sand - Granite: Hornfels Oacklands | n/a | n/a | 198 | 0.45 | n/a | 260-240 - BASF MasterPolyheed 8190 | 0-250 - BASF - MasterSet RT 122 | n/a | 0-750 - BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | 650(+-)100 | n/a | not supplied | not supplied | 12.7 | 570 |  | 0.029 | 2.421 | 70% | 70% | 72.25% |  |  |  | DTP Approved
|  |  |  | Holcim high SCM mixes & 40MPa with 70% .pdf | Holcim, 50MPa, 20mm ag, 120 slump | Holcim | In Progress | Not supplied | VE502EVR2 | S50 20MM VR450 120SL Ecopact Conc | 50MPa | n/a |  | 230 | CA - Goliath CMRS-ATIC 002 | 17.25 | 212.75 | 112 | Melbourne CMRS - ATIC-029 | 138 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 480 | 550 | 581 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 175 | 0.36458 | n/a | BASF MasterPolyheed 8190 | BASF - MasterSet RT 122 | BASF - MasterSet AC 534 | BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 52.08% | 58.18% | 61.32%
|  |  |  | Holcim high SCM mixes & 40MPa with 70% .pdf | Holcim, 50MPa, 10mm ag, 650 slump | Holcim | In Progress | Not supplied | VE501VWCH | S50 10mm 650SP 70% SCM Ecopact VR450 Conc | 50MPa | n/a |  | 144 | CA - Goliath CMRS-ATIC 002 | 10.8 | 133.2 | 150 | Melbourne CMRS - ATIC-029 | 186 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 480 | 550 | 709 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 190 | 0.39583 | n/a | BASF MasterPolyheed 8190 | BASF - MasterSet RT 122 | n/a | BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 70% | 73.82% | 75.78%
|  |  |  | Holcim high SCM mixes & 40MPa with 70% .pdf | Holcim, 55MPa, 20mm ag, 150 slump | Holcim | In Progress | Not supplied | VE552EVR3 | S55 20MM VR470 150SL Ecopact Conc | 55MPa | n/a |  | 245 | CA - Goliath CMRS-ATIC 002 | 18.375 | 226.625 | 98 | Melbourne CMRS - ATIC-029 | 147 | Independ Cem CMRS_ATIC-167 | 0 | n/a | 490 | 550 | 724 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 175 | 0.35714 | n/a | BASF MasterPolyheed 8190 | BASF - MasterSet RT 122 | n/a | BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 50% | 55.45% | 58.8%
|  |  |  | Holcim high SCM mixes & 40MPa with 70% .pdf | Holcim, 60MPa, 10mm ag, 650 slump, SPRD | Holcim | In Progress | Not supplied | VS601VSWC | S60 10mm VR520 Swork 650+- 100 SPRD Conc | 60MPa | n/a |  | 360 | CA - Goliath CMRS-ATIC 002 | 27 | 333 | 180 | Melbourne CMRS - ATIC-029 | 0 | n/a | 0 | n/a | 540 | 550 | 837 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 175 | 0.32407 | n/a | BASF MasterPolyheed 8190 | BASF - MasterSet RT 122 | n/a | BASF MasterGlenium SKY 8455 | n/a | n/a | n/a | n/a | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | not supplied | 33.33% | 34.55% | 39.45%
|  |  |  | VE502VWCH - VE502VWH4 - INTER - G4726-FA.pdf | Holcim, 50MPa, 550-800 slump | Holcim | G4726-FA | Not supplied | VE502VWCH / VE502VWH4 |  | 50MPa | n/a |  | 144 | CA - Goliath CMRS-ATIC 002 | 10.8 | 133.2 | 150 | Melbourne CMRS - ATIC-029 | 196 | Independ Cem CMRS_ATIC-029 | 0 | n/a | 490 | 550 | not specified | not specified | not specified | not specified | not specified | not specified | not specified | not specified | 180 | 0.36735 | n/a | n/a | 200-800 - BASF - MasterSet RT 122 | n/a | 1800-4300 - BASF MasterGlenium ACE 35 | n/a | n/a | n/a | 1000-3500 - BASF - MasterSure 1008 | 550-800 | n/a | T500 1 to 5 secs | <10mm | not supplied | not supplied | not supplied | not supplied | not supplied | 70.61% | 73.82% | 75.78% |  |  |  | DTP Conditional Approval
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A
[24 empty] | 0 | #N/A | [28 empty] | #DIV/0! | #N/A | #N/A

## Lists (hidden)
Grade | GBCA | VR Section 610 | AS 5100.5 | MRWA 820
20MPa | 280 | na | na | na
25MPa | 310 | na | 280 | na
32MPa | 360 | 330 | 330 | na
35MPa | 380 | 350 | 350 | 350
40MPa | 440 | 400 | 400 | 400
50MPa | 550 | 450 | 450 | 420
55MPa | 550 | 470 | 470 | na
60MPa | 550 | na | na | na
65MPa | 550 | na | na | 460
80MPa | 610 | na | na | na

## Drawing Note Examples (hidden)
TBC